## Calc Sheet
P602 - Basic Design Principles of Local Exhaust Ventilation Systems.
| Item | Ref/Equations | Units
1 | Duct ID |  | From-to
2 | Design Flowrate, 'Q' |  | m3/s
Slotted Hood?
(If 'yes' = row 3, if 'no' = row 10)
3 | Slot Velocity |  | m/s
4 | Slot Area |  | m2
5 | Slot VP |  | Pa
6 | Entry Loss Factor | 1.78 | -
7 | Acceleration Factor | 1 | -
8 | Plenum Loss Factor | Row 6 + Row 7 | -
9 | Plenum Sp | Row 5 x Row 8 | Pa
| Duct Diameter | √4xA/π | m
| Duct Area | Q/V = A | m2
| Duct Velocity | HSG 258 | m/s
10 | Available Duct Diameter |  | m
11 | Duct Area | πD²/4 | m2
12 | Duct Velocity | Row2 / row11 | m/s
13 | Duct VP | VP=(V/1.29)² | pa
14 | Duct Length | Drawing | m
15 | Friction Factor | Nomograph | Vp/m
16 | Actual Friction | row14 x row 15 | -
17 | Hood Entry Loss | Fig | -
18 | Acceleration Hood Fudge Factor | add value of 1.0 | -
19 | Elbows | Fig | -
20 | Branch Entry | Fig | -
21 | Other (a) |  | -
22 | Other (b) |  | -
23 | Other (c) |  | -
24 | Total Loss Factor | row 16 - row 23 | -
25 | Duct Sp Loss | row 13 x row 24 | Pa
26 | Other Equipment Losses (a) |  | Pa
27 | Other Equipment Losses (b) |  | Pa
28 | Preceding Junction (Index duct) |  | Pa
29 | Junction Vp Change |  | Pa
30 | Total Sp Losses |  | Pa
31 | Is this the governing Sp? |  | Yes/No