## Disclaimer
P601 Report Support
Disclaimer
This document has been provided with prompters to aid those without the required resources through completing the P601 Report submissions in harmony with the P601 Course notes. Using this document does not guarantee that you will pass. Although the calculations are automated and every effort has been made to makesure that they are correct, it is your responsibility to check the calculations are correct before submitting. It is also your responsibility to check that you have included all elements of the CoSHH ACoP and requests in the BOHS briefing document.
Congratulations if you have passed the first element of the BOHS P601. The BOHS will of sent you some information with your exam results to brief you on the next stage in obtaining your cetificate. This consists of undertaking 2 off Thorough Examination and tests of LEV Plant. This document has been provided by LEV Central for those who may not be familiar with LEV Testing. It is free lincence for you to utilise and chop & change as you see fit.
Theres no such thing as a free lunch…..
If you use this free resource and find it useful then please return the favour by adding a resource on
LEV Central website
LEV Central is a free to use website initiated by Bill Cassells and Louise Wood. It's upkeep is done in the little spare time we have. One of the ways you can support LEV Central is by placing an advert in our supplier directory. There is a small fee for doing this which helps us in covering annual webdesigner fees and updates.
Click here to be directed to our Supplier advert
Thank you

## Checklist
P601 Support
So you are ready to submit your two LEV Reports?
Number | Description | Check
1 | Handwritten site notes included for both tests?
2 | Reports typed up?
3 | Risk assessment and method statement included?
4 | Have you filled out the top sheets the BOHS supplied with your exam results?
Lost the top sheets? Download by following the link:
P601 report submission form

## Pg 1 LEV TExT Format
P601 Thorough Examination and Test Report
System ID: |  |  | Assessment of level of control
SATISFACTORY
Description of plant:
(See advisory recommendations)
Conclusions/Advisory recommendations
ID | Action required |  |  |  | Priority
Example | Train operators in the correct use of the LEV System |  |  |  | High
*Priority – e.g. 1 = high, 2 = normal, 3 = routine
Report prepared for |  |  | Report prepared by
Client name |  |  | Company name
Client address |  |  | Address
Introduction
Purpose of test |  |  | Date of this test
Date of last test
Test frequency
Review since the last examination and test
Have the materials processes changed
Have the work procedures changed
Has the system layout changed
Available documentation
Commissioning report |  |  | MSDS Sheets
User manual |  |  | Log book
System Details
The purpose of this system is to
Process
Status of the process at time of test
Process and substances being controlled
Potential health effects from breathing in the substance (s)
Substance(s) being extracted |  | Workplace exposure limit(s) |  |  |  | Exposure benchmark
|  | 8hr TWA (Inhalable) |  | 8hr TWA (Respirable)
* Reference EH40/2005, Workplace Exposure Limits.
Are the substances flammable
Are the substances explosive
Fan Specification
Fan type |  |  | Electrical supply
Manufacturer |  |  | Motor size |  |  |  | kW
Model |  |  | Full load current
Serial number |  |  | Motor speed (approx) |  |  |  | RPM
Type of impeller |  |  | Impeller speed (approx) |  |  |  | RPM
Condition of fan |  |  | Impeller direction of rotation
Type of drive |  |  | Differential pressure:
Notes:
Filter Specification
Filter type |  |  | Filter media type
Manufacturer |  |  | Filtration area
Model |  |  | Condition of filter media
Serial number |  |  | Differential Pressure
Condition of filter
Suitability of position of unit
Notes:
Duct Details
Condition of duct
Suitability of ductwork
Notes:
Stack/Discharge Details
Type of stack/discharge
Suitability of discharge
Notes:
Make up air details
Is there adequate make up air
Induced drafts
Notes:
Note on E10: Louise Airducts: System number; 1, 2, 3, 4, 5 etc
Note on J11: Louise Airducts: OPTIONS: -SATISFATORY -UNSATISFACTORY
Note on E12: Louise Airducts: Brief description of plant, for example: - Dust extraction system serving the sieving. - Laboratory fume cupboard - Welding fume extraction
Note on A29: Louise Airducts: Pretty self explanatory. Your client/site details need to be detailed here.
Note on J29: Louise Airducts: Self explanatory. This is the details of the company you work for
Note on M38: Louise Airducts: The date you did the LEV TExT
Note on M39: Louise Airducts: The date of the last LEV TExT. If not known, simply enter NOT KNOWN.
Note on M40: Louise Airducts: This is the test frequency: 14 months - Most systems should be tested at least once in a period of every 14 months. There are exceptions to this detailed in Table 18 of HSG258; Legal maximum intervals for thorough examination and test of LEV Plant used in certain processes (CoSHH Schedule 4): 1 months - Processes in which blasting is carried out in or incidental to the cleaning of metal castings in connection with their manufacture. 1 months - Jute Cloth manufacture. 6 months - Processes other than wet processes in which metal articles (other than gold, platinum or iridium) are ground, abraded or polished using mechanical power in any room for more than 12 hours a week. 6 months - Processes giving off dust or fume in which non-ferrous metal castings are produced.
Note on G56: Louise Airducts: Were the operators using the plant whilst you were testing? i.e. Was it operational or non-operational
Note on F61: Louise Airducts: I.e. Is the substance a Carcinogen, Asthmagen. What diseases occur from exposure? i.e. COPD, Silicosis. This can be found in the MSDS Sheet.
Note on A67: Louise Airducts: Enter the substance name here. Reference the MSDS sheet or EH40 to find out the exposure limits to fill out the cells in the adjoining columns.
Note on O67: Louise Airducts: Follow the exposure benchmark as taught in the P-Cert course or use the industry standard of 1 tenth of the Workplace Exposure Limits (WEL). The purpose of this is to find out if the hood is acceptable against the CoSHH Benchmark model.
Note on A76: Louise Airducts: The fan information can normally be found on a Rating plate on the fan casing or from the motor rating plate. Sometimes both the fan and motor do not have rating plates and this information is unavailable.
Note on F83: Louise Airducts: Motors are generally one of the following drive types: - Direct driven. - Gear driven. - Belt driven.
Note on O83: Louise Airducts: This is simply the sum: a = b - c a = differential pressure b = Fan inlet duct (Upstream) c = Fan outlet duct (Downstream)
Note on A87: Louise Airducts: The filter specification can normally be found on Rating plates/data sheets or user manuals.
Note on O88: Louise Airducts: Cartridge, Polyester pocket, PTFE or other coatings.
Note on O91: Louise Airducts: This is simply the sum: a = b - c a = differential pressure b = cleanside pressure c = dirtyside pressure
Note on F94: Louise Airducts: Are the access doors accessible for maintenance. If there is an explosion vent, does it vent to a safe place? Where does the filter unit discharge it's filtered air? If inside: - Is there suitable secondary filtration of HEPA grade if discharging into the workplace? - Do the filters require a particulate count? If that has not been done as part of your LEV assessment then put it as a recomendation at the top of this page.
Note on F99: Louise Airducts: Is the duct damaged, are seals perished? These can all add up to additional resistance that the fan perhaps may not have the capacity to handle.
Note on F100: Louise Airducts: Is the duct good design? Is the duct the right material for the substance used? Too much flexible hose used?
Note on F105: Louise Airducts: Vertical or horizontal discharge? Via a grille at the top of the dust filter?
Note on F106: Louise Airducts: Is the stack tall enough? Where does it discharge? Is there a risk of dust or fume re-entering the building?
Note on F111: Louise Airducts: Make up air could be mechanically installed air input. Roof fans, air vents in the roof, walls, doors or even windows. If air cant come in, it cant go out. You will know if there is insufficient makeup air if the doors are difficult to open/close.
Note on F112: Louise Airducts: Tracer smoke can be a useful indicator of draughts that effect the hood. Use with care as could set off fire/smoke alarms etc. Look out for desk fans. These stop the hoods from working.

## Pg 2 LEV TExT Format
Schematic sketch
System Photos
Note on A1: Louise Airducts: There are several platforms you can use to produce a schematic drawing of an LEV Plant. i.e: - Excel or word drawing tools - Draft Sight, a free to use CAD software with an interface very similar to major 2D CAD suppliers. Simply select the schematic, right click and select copy in Draft Sight and then visit excel and paste. Crop and alter as required. - Smartdraw - Paint - Can even draw by hand and scan/photograph and add into this document.

## Pg 3 LEV TExT Format
NOTE Highlighted yellow means input. This will calculate cross sectional area and volume for you
Quantitative test results
Test Point | Duct dimensions | [6 empty] | Cross sectional | Velocity (v) | Volume flow |  | Static Pressure | Commissioning Data
ID | Dia | Square duct | [5 empty] | Area | M/s | M/3s | M/3h | Pa | Date | Pa | M/3h
TP1 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP2 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP3 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP4 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP5 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP6 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP7 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
TP8 | 0 |  | x | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Hood Results
Qualitative hood results
Efficiency
Test Point | Hood dimensions | [6 empty] | Cross sectional | Static Pressure | Hood type | Assessment technique | Capture | Control Effectiveness
| Dia | Square duct | [5 empty] | Area | Pa |  |  | distance
H1 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H2 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H3 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H4 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H5 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H6 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H7 | 0 |  | x | 0 | 0 | 0 | 0 | 0
H8 | 0 |  | x | 0 | 0 | 0 | 0 | 0
Test point and hood result summary
Equipment used for assessment
Is the system still maintaining satisfactory performance?
The Methods used to judge performance
Note on K4: Louise Airducts: If you have taken multiple velocity readings along a traverse then simply enter the mean average.
Note on O4: Louise Airducts: If you have the commissioning or Initial test data then enter this in these three columns
Note on L18: Louise Airducts: Capture, Receiving, Partial enclosure or full enclosure
Note on M18: Louise Airducts: Tracer smoke or tyndall lamp
Note on K30: Louise Airducts: Self explanatry really but use this section to detail the tools and equipment used here
Note on K34: Louise Airducts: This only applies if the system has been tested previously.
Note on K35: Louise Airducts: Did you take several reasings across a hood face or along the traverse of a duct. If you measured the capture distance using tracer smoke then explain how you did it.